Qi Application note

Interfacing to the Qi Matroller platform

Best Practices and Items of Note

Target audience:

- System Integrators

- Project Managers

The following topics deal with interfacing your application to a Qi Matroller. This Application note attempts to highlight and explain some but not all of the aspects of interfacing to the Qi.

Reference’s:

Sharedat.doc		(document listing all Shared Data variables within a Qi Matroller)

Apc_Mesg.doc	(document detailing the communications interface of the Qi M)

A16506600A.pdf	(official Qi Matroller technical manual)

Qi Technical Manual 	(same as A16506600A)

These documents are available for downloading from:  ftp://ftp.usa.mt.com/pub/indmkg/Qi FTP Support Site/

Index

Ready to Start a Feed ??	2

Time interval between sending commands to the Qi Matroller	3

Matching the Command sent with the Response read	4

Getting out of Synchronization (Lockstep)	5

Are we “In Control” ?	6

Ready to Start a Feed ??

A question that is often asked is, how do I know that the Qi is ready to accept a Start Feed command ?

Answer:

Within the cyclic data being read from the Qi are a number of status bits. If they are in the correct state you can be 99% sure that the Qi will accept a Start Feed command. What about the 1%? Well the command may be invalid ie you are asking the impossible or the command may be part of an Overlapping Feed sequence, which means the actual start is delayed until the sequence is completed.

In the second byte of the cyclic (scheduled) channel data sub block there are 8 status bits labeled as follows:

- “PAC Data Integrity Bit” alternates polarity every 5 seconds.

- “Instrument Data Integrity OK “

- “Scale Over Capacity”

- “Scale Under Zero”

- “Scale Motion”

- “Material Transfer Cycle Active”

- “Final Control Element Output”

- “Waiting for Controller to Acknowledge Last Material Transfer/Hand Add complete”

In addition to these bits there is one more in the next word following. It is the 3rd bit and is labeled “Manual/Not Auto mode” This bit should be 0

NOTE: these 8 status bits exist for each channel !

If these bits are in the state listed below you can be 99% sure that the Qi is OK to start feeding

PAC Integrity bit		don’t care

Instrument Data Ok		ON

Scale over capacity		OFF

Scale under zero		OFF

Scale in motion		OFF

Material transfer active	OFF

FCE output			OFF

Waiting for “Ack”		OFF

Manual/Not Auto-Mode	OFF		(bit 3, next word)

NOTE: if the Waiting for Ack bit is ON your application must send an Ack Command (4)

NOTE: Your application should also be monitoring the toggling of the PAC integrity bit. If this bit stops toggling you should stop feeds for that channel and also stop any “Start Feed” commands from being sent.

## Time interval between sending commands to the Qi Matroller

Question:

What is an acceptable time delay between sending commands to a Qi Matroller

Comment:

The time a Qi takes to act on a command and prepare a response varies. If the final destination of the command is local to the bridge Qi then the Qi will have a response ready in about 60 mS.

If the final destination is a flow meter on a remote Qi then the response could take as long as 350 mS as it has to be routed to another Qi etc. These hops all add overhead.

A distinction between a scale and flow meter is made as a scale will always respond quicker due to it being a higher priority task.

Answer:

After sending a command we would recommend waiting for about 70 to 80 mS before reading the command response. HOWEVER you must make sure that if you get a response number 6 (Command Not Complete – Request status again after a short delay ) your application must then go into a loop. Wait for 80 mS and read again etc etc. Until you get a valid response (not a 6) Obviously this loop must have a finite number of iterations!

## Matching the Command sent with the Response read

Question:

Once a command is sent to a Qi, it is recommended that you then read what the Qi had to say about the command that you just sent! It may not have liked the command

.

But how do you know whether you are reading the current command’s response or the previous command’s response?

Answer.

The first four fields of the response contain the first four field of the command. These four fields should be compared with each other. Then, only once you see a match do you update the command response to the relevant command.

## Getting out of Synchronization (Lockstep)

Practical experience has shown us that it is possible for the main PLC/Controller application to get out of Sync with the Qi Matroller.

What typically happens is that the Controller application is stepping through a sequence of events. At sequence step x it sends a “Start Feed” to the Qi and then moves on to step x + 1. However, should the Qi reject the command for whatever reason then the application is now in step x + 1. Which is now out of sync with the Qi which is now waiting for another “Start Feed” command, which can only be issued by the application when it is in step x.

Care must be taken to ensure that the application can recover and go back to step x when the Qi rejects the “Start Feed” command.

If the command was rejected due to an excessive movement of the scale, then in all likely hood the Qi will accept the next Start Feed command. Unless of course a mixer has become unbalanced and the scale is subject to excessive vibration. In this case the cause must be fixed.

If the command was rejected due to an invalid parameter, such as a too large or too small a target value, or an incorrect Material Path. Then the application should go back to step x and the operator must be given the opportunity to repair the command.

## Are we “In Control” ?

When using a Qi Matroller we are subscribing to distributive control. And as such it is  very important that the host controller monitors the state of the remote control device (in this case the Qi Matroller.

Should the host controller notice that the Qi is not responding “normally” it should immediately stop the flow of material until the situation is clarified. This of course implies that the host controller is able to stop the flow of material! In all cases the host controller must have an O/P that is in series with the QI’s O/P. This allows the host controller to have the “final say” when it comes to enabling the flow of material. This is normally termed the “Material Path Matrix” or “Material Path Enables”.

It is normal to find this matrix in place for an analogue scale, but it is also important that a host controller also has an O/P in series with a Flowmeter channel even though there is normally only one material per Flowmeter. This will then allow the host controller to also have final say when it comes to flowmeter additions.

How do we recognize that there is something amiss with the Qi Matroller? Well there are a number of things that we can and must monitor.

Total communications failure.

All host controllers can recognize when a device has gone “offline”. System bits exist within controllers to warn of such an event. These bits must be monitored and acted upon. The reasons for the failure can be many. Ie Loss of power to the Qi, failure of a major component in the Qi, a cable break etc.

NOTE: The response time for reacting to this type of failure is fairly quick, in the order of a second or two depending on the system parameters

Faulty instrument

An “instrument OK” bit exists for each and every instrument in the cluster. If the QI recognizes that the instrument has failed it will turn this bit OFF. These bits must be monitored and acted upon.

NOTE: The response time for reacting to this type of failure is fairly quick, in the order of a second or two.

Toggle bit

There is a bit for each channel that alternates every few seconds. This “PAC data integrity” bit must be monitored and acted upon, should it stop alternating.

NOTE: The response time for reacting to this type of failure is fairly slow, depending on how the user application is written this delay could extend to as much as 25 seconds before the system recognizes that there is a failure.

Slow Feeds

Should a feed take too long to complete the operator should be notified immediately. The Qi Matroller can be setup to either ignore the fact that the Slow Step timer has timed out, or it can be configured on a Material by Material basis to automatically Abort the feed when the Slow Step timer, times out. This factor can be individually set for each Material.

The cause for the time out could simply be a low flow, or lack of material. Or something much more serious such as a faulty loadcell, a faulty flowmeter,  aeration of product resulting in an under totalization of product or pulses that are not reaching the Qi due to a cable break. Each of these is serious, as the product will continue to flow, past its target by an undetermined amount. Any material that has dire consequences should this happen should be dealt with appropriately.

NOTE: The response time for reacting to this type of failure is very slow, and is very dependent on where you are in the feed and how large your factor is set at.

Low Flow

Although the Qi does not provide a “Low Flow” signal, the actual Flow Rate of the material is made available to the host controller. For critical materials it would be prudent to include a “Low Flow” warning for the operators. This state can easily be calculated by the host controller.

NOTE: The response time for reacting to this type of failure is very slow, and is very dependent on how the user application has been programmed to recognize this eveny.